## IM B3
Z
Specification | IEC 60034-1 |  |  |  | Efficiency class
Manufacturer | Felm srl |  |  |  | Load data |  | 100% | 75% | 50% | 25%
Motor type | IE2-280M-6 |  |  |  | Efficiency |  | 93.4 | 93.3 | 92.3 |  | %
Rated power | 55 | kW | S1 | duty | Power factor |  | 0.86 | 0.86 | 0.79
Speed | 990 | r.p.m
Voltage | 400/690 | V |  |  | Sound pressure level (1m) | [5 empty] | dB(A)
Frequency | 50 | Hz |  |  | Resistance R20 (open) | [5 empty] | W
Connection | △/Y |  |  |  | Full load torque |  |  |  |  | 530.5556 | Nm
Amps full load | 102.7/59.6 | A |  |  | DOL Starting torque vs FL torque |  |  |  |  | 2.1
Amps no-load(400V) |  | A |  |  | DOL Pull up torque vs FL torque
Enclosure | IP55 |  |  |  | DOL Pull out torque vs FL torque |  |  |  |  | 2.7
Insulation Class | F(temp.riseB(80K)) |  |  |  | DOL Starting current vs FL current |  |  |  |  | 6.5
Cooling | IC411 |  |  |  | Grease | type |  | SRI-2
Max. coolant temp. | 40℃ |  |  |  | Grease Quantity DE |  |  |  |  | 50 | gr
Max. altitude | 1000 | mtr, above sea level |  |  | Grease Quantity NDE |  |  |  |  | 50 | gr
Comment |  |  |  |  | Grease Interval |  |  |  |  | 2000 | h
Cable entries | 2-M63X1.5
Feature | Cast-iron motor
Rotor Inertia | 1.965 | kgm2
Weight | 565 | kg
Catalog no. |  |  |  |  | Bearing DE |  |  |  | 6317 C3
Warranty |  |  |  |  | Bearing NDE |  |  |  | 6317 C3
Extras / Options : |  |  |  |  | WI | Change |  |  |  | date | sign.
0 | [7 empty] | Discription |  | date | sign.
0 | [7 empty] | Drawing made by : |  | 07.3.20
0
0
0