Comelmar Italia

DA T A   S H E E T

SLIP RING INDUCTION MOTOR

Type:	CMA 560-8	Reference standard:	IEC 34-1

Output (kW):	900

Stator voltage (V):	400

Stator current (A):	1606

Rotor voltage (V):	840

Rotor current (A):	665

Frequency (Hz)	50

Stator connection	DELTA

Rotor connection:	STAR

Speed (r.p.m):	742	Direction of rotation viewed from DE:	BOTH

Protection degree motor:	IP 55

Mounting:	IM B3

Bearings type:	      ANTIFRICTION

Lubrication:	GREASE

Insulation class:	F

Cooling:	IC 611

*Efficiency at : 4 / 4 load (%)	95.3

Efficiency at : 3 / 4 load (%)	95.1

Efficiency at : 1 / 2 load (%)	94.4

*Power factor at: 4 / 4 load	0.85

Power factor at: 3 / 4 load	0.81

Power factor at: 1 / 2 load	0.73

*Break-down torque:	2.5

Max. altitude(a.s.l):	1000

Ambient :  max. temperature (°C)	40

humidity at 20°C (%)	80

Estimated weight (kg):	8500

GD2 (kgfm2):	620

Rated duty	S1

Dimensions drawing	IG56-

Stator winding RTD's	6 x Pt 100 ohms at 0 °C(2/phase)

Bearings RTD:	2 x Pt 100 ohms at 0 °C(1/bearing)

Space heater:	         500W, 220V, a.c

The values marked with  *  are guaranteed within the limits of tolerances specified in

IEC 34-1.