## DS Sheet 1
Electrical Data Sheet
Manufacturer |  | FELM s.r.l.
Reference Standards |  | EN-IEC 60034
Tests to be performed according |  | IEC
Motor type |  | 315X-4
Quantity
Rated power | kW | 315
Rated speed | rpm | 1485
Mechanical arrangement
Rated torque | Nm | 2025.7576
* Starting torque | Nm | 1.5
* Break down torque | Nm | 2.0
Cooling method | IC | IC411
Degree of protection | IP | 55
Rotor inertia | kgm2
Motor weight | kg | 1450
Winding insulation process
Rated voltage | V | 400/690
Rated current | A | 547/317
Rated frequency | Hz | 50
Winding connection |  | △/Y
Rated efficiency | % | 95.5
Rated power factor |  | 0.87
* Starting current | % | 700
Starting time at 100% voltage | sec
Starting time at 90% voltage | sec
Starting current at 100% voltage | A
Starting current at 90% voltage | A
Duty |  | S1
Service factor |  | 1
Insulation class |  | F
Temperature rise class |  | B
Bearing type (DE/NDE) |  | 6319C3/6319C3
Lubrication |  | SRI-2
Frame
Air-air cooling
Terminal box
Fan
Fan cover
Direction of rotation looking at drive end
Vibration grade
Noise pressure level at 1mt at full load | d B(A) | 91
Driven machine
Inertia of the driven machine (kgm²)
Painting
Climate
Relative humidity
Installation environment
Plant altitude (a.s.l.)
Min ambient temperature |  | -20°C
Max ambient temperature |  | 40°C
Operating schedule
Marking --- Supplier quality Assurance
Noise level evaluation
ACCESSORIES
Space heater rated voltage and tolerances. | V/kW
Windings thermals detectors |  | 3XPTC150°C
Bearing thermals detectors
Cooling air pressure
Air cooling thermal switch
* Note: PERFORMANCE TOLERANCES ARE IN ACCORDANCE WITH IEC 34-1