| Electrical Data Sheet |  |  |
| --- | --- | --- |
| Type |  | Y500-10 560kW 6kV 50Hz |
| Weight | kg | 4480 |
| Standard |  | EN-IEC 60034 |
| Output Power | kW | 560 |
| Votage | V | 6000 |
| Votage Tolerance | % |  |
| Connection |  | Y |
| Frequency | Hz | 50 |
| Frequency Tolerance | % |  |
| Poles |  | 10 |
| Rated Speed | rpm | 590 |
| Slip | % | 1.667 |
| Rated current | A | 71.9 |
| Rotor current | A |  |
| Rotor voltage | V |  |
| Non load current | A |  |
| Rated tourque | Nm | 9064 |
| Degree of Protection | IP | IP23 |
| Vibration | mm/s | 2.8 |
| Mounting |  | IMB3 |
| Cooling |  | IC01 |
| Altitude | m | 1000m |
| Max. ambient temperature | °C | -20～40°C |
| Insulation Class |  | F |
| Temperture Rise |  | 80K |
| Service factor |  | 1.0 |
| Duty |  | S1 |
| Application Load |  |  |
| Starting Methode |  | DIRECT ON LINE |
| Coupling |  | DIRECT |
| Direction of Rotation |  | Both |
| DE Bearing type |  | 6330C3 |
| NDE Bearing type |  | 6328C3 |
| Hazardous Area |  |  |
| Space Heater | V | 220 |
| PT100 per phase | pcs | 2 |
| PT100 per bearing | pcs | 1 |
| Brushes |  |  |
| Balancing |  |  |
| Max. sound level | dB(A) | 88 |
| Rated efficiency | % | 93.7 |
| Rated power factor |  | 0.8 |
| Output 50% - Efficiency | % | 90.9 |
| Output 50% - Power Factor |  | 0.68 |
| Output 75% - Efficiency | % | 93.9 |
| Output 75% - Power Factor |  | 0.76 |
| Output 100% - Efficiency | % | 93.7 |
| Output 100% - Power Factor |  | 0.8 |
| Locked Rotor Current | % | 550 |
| Locked Rotor Torque | % | 80 |
| Breakdown Touque | % | 180 |
| Outline |  | Y500-6～12P 3～7kV |