## ＤＡＴＡ
SIMOTOP GROUP SPA
Data Sheet | [6 empty] | No.
Three Phase Induction Motor | [6 empty] | Drawing No.
Customer
Client reference
Type: |  |  |  | Y450-2 1000kW 6kV 50Hz(SIMOTOP)
Brand
Identification
Frame: |  |  | 450 |  | mm | Insulation Class: |  | F
Output: |  |  | 1000 |  | kW | Temperature Rise: |  | 80K
Frequency: |  |  | 50 |  | Hz | Service Factor: |  | 1
Poles: |  |  | 2 |  | P | Duty: |  | S1
Rated Speed: |  |  | 2970 |  | rpm | Ambient Temperature: |  | -20～40°C
Slip: |  |  | 1 |  | % | Altitude: |  | 1000m
Rated Voltage: |  |  | 6000 |  | V | Protection Degree: |  | IP23
Connection: |  |  | Y |  |  | Cooling: |  | IC01
Rated Current: |  |  | 114.6 |  | A | Mounting: |  | IM B3
Rotor Voltage: | [5 empty] | Vibration: |  | 2.8 mm/s
Connection: | [5 empty] | Approx. Weight: |  | 3500 | kg
Rotor Current: | [5 empty] | Moment of Inertia: |  | 52.1 | kg/m2
Locked Rotor Current: |  |  | 700 |  | % | Noise Level（Lp）: |  | 95 | dB(A)
No Load Current: | [5 empty] | Direction of Rotation: |  | CW
Rated Torque: |  |  | 3215 |  | Nm | Starting Method: |  | DIRECT ONLINE
Locked Rotor Torque: |  |  | 55 |  | % | Coupling: |  | DIRECT
Breakdown Touque: |  |  | 210 |  | % | Load Type: |  | PARABOLIC CURVE
Performance | [5 empty] | Bearing Information
Output: |  | 50% |  | 75% | 100% |  |  | DE | NDE
Efficiency(%)： |  | 92.538 |  | 95.4954 | 95.4 | Bearing: |  | 6222C3 | 6222C3
[6 empty] | Regreasing int.(h): |  | 4000 | 4000
Power Factor: |  | 0.748 |  | 0.836 | 0.88 | Grease amount(g) |  | 50 | 50
[6 empty] | Grease-PolyrexEM |  | SRI-2# | SRI-2#
Notes / Accessories | [5 empty] | Deviation Sheet
With winding PT100，6PCS
With bearing PT100 2PCS
With heater 230V
VFD:25-50HZ
Insulated bracket at NDE
Standards | [6 empty] | PRELIMINARY DOCUMENT
Specification: |  | IEC60034-1
Test: |  | IEC60034-2
Noise: |  | IEC60034-9
Vibration: |  | IEC60034-14
Edition
Performed |  | Checked |  |  | Date
Item | Changes | [5 empty] | Performed | Checked | Date